## ahuMdl
| dtCc | dtHc | oaFrac
0 | -15.7093 | 2.4275 | 0.41079
1 | -11.9838 | 3.8459 | 0.2371

## faults
| AHU Health Index | Cooling coil | Economizer | Heating Coil | Outdoor Air Damper | Perimeter heating in Econ Mode | Schedule
0 | 66.6667 | Normal | Normal | Normal | Low outdoor air | Add a low limit to the economizer mode availability | Normal
1 | 50 | Normal | Normal | Normal | Low outdoor air | Add a low limit to the economizer mode availability | No schedule